Electrical Code Interpretation SFEC 2007-2

June 19, 2008

Subject:

Protection from Physical Damage

Question:

Shall Type MC Cable, #4 AWG or larger, be considered protected from physical damage when installed

in a lockable room dedicated to electrical service and distribution equipment and accessible only to

qualified personnel?

Reference:

San Francisco Electrical Code (SFEC) 2007 Edition Section 330.12, Article 100 Definitions

Existing Text:

Section 330.12 Uses not permitted.  Type MC Cable shall not be used where exposed to the following

destructive corrosive conditions, unless the metallic sheath is suitable for the conditions or is protected

by material suitable for the conditions:

(1) Where subject to physical damage

(2) Direct Burial in the earth

(3) In concrete (FPN)

(4) Where subject to cinder fills, strong chlorides, caustic alkalis, or vapor or chlorine or of hydrochloric

acids.

Article 100 Definitions, Subject to physical damage. Wiring installed within 2.44 m (8 feet) of a walking

surface or finished floor is considered subject to physical damage.

Discussion:

Type MC Cable #4 AWG or larger, installed in a lockable room dedicated to electrical service and

distribution equipment and accessible only to qualified personnel, shall be considered to have

equivalent protection from physical damage when installed in a neat and workmanlike manner, properly

supported, and securely fastened in place.

Michael Hennessy, Chief Electrical Inspector

CC:	Isam Hasenin, P.E. CBO Director
Ron Allen, Senior Electrical Inspector
David Green, Senior Electrical Inspector
Henry Hinds, Senior Electrical Inspector
Paul Ortiz, Senior Electrical Inspector
EID Inspection Personnel
File copy