INFORMATION SHEET

NO.  FS-07

DATE	:	November 17, 2015

SUBJECT	:	Fire Safety

TITLE	:	Elevator Lobbies in High-Rise Buildings

PURPOSE	:	The purpose of this Information Sheet is to restrict movement of smoke and heat between floors through elevator doors and hoist-ways.

REFERENCES	:	CBC-2013: Section 713.14.1 Exceptions 2-8

CBC-2013: Section 1008.1.2 Exception 6

Exceptions listed in the above referenced codes shall not be applicable to high-rise buildings.

REQUIREMENTS	:

Elevator lobbies in high-rise buildings shall be enclosed with 20-minute rated doors and shall be of the pivoted or side-hinged swinging type.

Lobbies that serve Fire Service Access Elevators shall be enclosed with 45-minute rated side-hinged swinging type doors.

Existing side-hinged swinging doors in high-rise elevator lobbies shall not be removed.

In existing non-conforming high-rise buildings where elevator lobbies are unenclosed, the installation of listed products complying with 2013 CBC 713.14.1 Exceptions 5 or 8 shall be acceptable.

______________________________________________

Daniel de Cossio		Date

Fire Marshal & Assistant Deputy Chief

San Francisco Fire Department

_________________________________________________

Tom C. Hui, S.E., C.B.O.			Date

Director

Department of Building Inspection

# Text boxes

This Information Sheet is subject to modification at any time. For the most current version, visit our website at http://www.sfdbi.org