INFORMATION SHEET

NO.  P-03

DATE	:	November 7, 2016

SUBJECT	:	Plumbing

TITLE	:	Water Conservation of Commercial Buildings

PURPOSE	:	The purpose of this Information Sheet is to clarify how to self-certify the water conservation by improving the water efficiency of commercial buildings no later than January 1, 2017.

REFERENCES	:	San Francisco Building Code Chapter 13A

Ordinance No. 77-09

DISCUSSION	:

- Per SFBC Section 1306A.3, on or before January 1, 2017, all commercial buildings shall be in compliance with SFBC Chapter 13A, and the owner or the owner's authorized representative shall cause a water conservation inspection to be completed, and shall have a certificate of compliance on file with the Department of Building Inspection for the entire building, or the entire portion of the mixed residential and commercial building that is subject to the required water compliance measures identified in SFBC Section 1313A.

- Commercial buildings include but not limit to:

  - Commercial buildings;

  - Any portion of a residential building, which is used for commercial purposes;

  - Any portion of a residential building converted to a tourist hotel;

  - Any portion of a residential building which is occupied as a hotel or motel unit and which has a certificate of use for tourist occupancy;

  - Any building or portion thereof which is a live/work occupancy;

- Water Conservation Measures Requirements

| Fixture | Measure Requirement |
| --- | --- |
| Showerheads | Flow rate ≤ 2.5 gallon per minute (gpm) |
|  | No more than one showerhead per valve |
| New showerhead installation | Flow rate ≤ 2.0 gpm |
| Faucet and Faucet Aerators | Flow rate ≤ 2.2 gpm |
| New kitchen faucet installation | Flow rate ≤ 1.8 gpm |
| New residential lavatory faucet installation (includes hotel guest rooms) | Flow rate ≤ 1.2 gpm |
| New public lavatory faucet installation | Flow rate ≤ 0.5 gpm |
| Toilets | Water consumption ≤ 1.6 gallons per flush (gpf) |
| New toilet installation | Water consumption ≤ 1.28 gpf |
| Urinals | Water consumption ≤ 1.0 gpf |
| New urinal installation | Water consumption ≤ 0.125 gpf |
| Leaks | All plumbing leaks must be located and repaired. |

- The owner or the owner's authorized representative shall cause a water conservation inspection by the owner, the owner’s representative or an engineer, and shall have the Commercial Water Conservation Affidavit and Self-Certification Form (“the Form”) (see Attachment A for the Form) signed by the owner, the owner's authorized representative or an engineer. Inspection by DBI Plumbing is optional.

- The owner or the owner's authorized representative can download the Form from our website: http://sfdbi.org/forms-handouts.

- The owner or the owner's authorized representative can submit the Form to email address: dbi.plumbing@sfgov.org, or by visiting DBI’s Commercial Water Conservation counter at Window #8, located at 1660 Mission Street, San Francisco, 1st floor.

- The owner or the owner's authorized representative shall have the Form on file with the Department of Building Inspection on or before January 1, 2017.

OTHER CONDITIONS:

Other conditions will be evaluated on a case-by-case basis by the Chief Plumbing Inspector or his designee.

_________________________________________________

Tom C. Hui, S.E., C.B.O.			Date

Director

Department of Building Inspection

Attachments: Commercial Water Conservation Affidavit and Self-Certification Form

# Comments

effective July 1 2016

# Text boxes

This Information Sheet is subject to modification at any time. For the most current version, visit our website at http://www.sfdbi.org